COMUSFLTFORCOMINST 4790.3 REV B


NUCLEAR/NON-NUCLEAR
PRE-TEST INSPECTION CHECK LIST

References:
(a)
NAVSEA S9505-AF-MMA-010 - Piping Systems/Submarine Non-Nuclear Piping Systems Test Manual

(b)
NAVSEA 0387-LP-046-8000 - System Hydrostatic Test Requirements

	ITEM NO.
	ATTRIBUTE
	CHECK OFF

or N/A

	1.  REVIEW TEST PREPARATIONS:  The following attributes are necessary for proper test accomplishment and may be included in the test procedure, indicated on the Quality Assurance (QA) form 26 or covered in the pre-test briefing.

	a.
	Test equipment installation location and method of installation is clearly indicated in sketch on the QA form 26, or is clearly defined.  Test accomplishment will be in accordance with reference (a).
	

	b.
	Specific jumpers/gagging devices/blanks etc. are indicated for both installation and removal.  These items shall be danger or caution tagged.
	

	c.
	Boundaries of test and specific inspection points are clearly identified.  
	

	d.
	Instructions are provided for returning the system to normal or to a specifically stated condition upon completion of the test.
	

	e.
	Procedure minimizes the amount of system to be pressurized to accomplish the test.  
	

	f.
	All components within the test boundary are capable of withstanding the test pressure (gages not over-ranged, etc.). 
	

	g.
	Necessary precautions as identified on the test pressure drawing have been taken (List or none).  Use reverse if additional space required.
	

	
	
	

	
	
	

	
	
	

	h.
	Applicable chapter (maintenance section) or maintenance instruction of the RPM reviewed for test/flush requirements (List or none).  Use reverse if additional space required.  (Not applicable to non-nuclear tests.)
	

	
	

	
	
	


	ITEM NO.
	ATTRIBUTE
	CHECK OFF

or N/A

	i.
	Specific actions/precautions taken are included in the test procedure as a result of a review of reference (b), sections 7.2.3, 7.2.4 and 7.2.5 to preclude damage to installed system components due to pressure or temperature conditions that may occur during the test (List or none).  Use reverse if additional space required

(Not applicable to non-nuclear tests).
	

	
	

	
	

	
	
	

	2.  WALKTHROUGH OF THE TEST AREA:  The below listed attributes are basic quality control checks that should be conducted/supervised by the Petty Officer in charge of the test. 

	a.
	Piping in the test boundary is free from dents, gouges, arc strikes and other external defects (Removal of additional lagging or other interference is not required to perform this check).
	

	b.
	Conditions for detecting leaks are satisfactory (e.g., joints being tested are not covered/lagged).
	

	c.
	Hot piping and/or equipment that could result in a safety hazard to personnel has been insulated or precautions have been taken to minimize the hazard.
	

	d.
	The hydrostatic test will not be a hazard to other evolutions adjacent to the test area (e.g., Work on an open oxygen system adjacent to a seawater hydro).
	

	e.
	Adequate measures have been taken to prevent spray damage to electrical equipment in the event of a leak during pressure testing.
	

	f.
	Pipe hangers removed for work have been reinstalled.
	

	g.
	All mechanical joints are re-made; system integrity established.
	

	h.
	No obvious loose fasteners.
	

	i.
	No obvious instances of missing fasteners or improper fastener material or material mismatch (e.g., no carbon steel fasteners in seawater systems, no improper use of black oxide coated fasteners).
	


Completed by                                Items Completed                               Date 

Completed by                                Items Completed                               Date 

Reviewed (Div Off/EDO)                                                                       Date 

